NABH/GEN/2026/00009 	January 02, 2026

# Fire Safety Advisory for Healthcare Organizations (HCOs)

Dear Healthcare Organizations (HCOs),

New Year Greetings from NABH!

The New Year marks a time for renewed resolutions, commitments, and dedication. In line with its continuous efforts to strengthen quality and safety in the healthcare sector, the National Accreditation Board for Hospitals & Healthcare Providers (NABH) has earmarked the month of January as Fire Safety Month to reinforce fire safety measures across healthcare organizations.

During this period, hospitals are encouraged to enhance fire safety preparedness through focused awareness programs, staff training, mock drills, and necessary system upgrades. This initiative aims to strengthen compliance with fire safety norms, ensure a safer hospital environment, and improve emergency preparedness, thereby contributing to enhanced patient safety, staff safety, and the overall quality of healthcare services.

Fire safety is a paramount concern for all healthcare facilities, ensuring the safety of patients, staff, and visitors alike. Recognizing this critical aspect, the National Accreditation Board for Hospitals & Healthcare Providers (NABH) underscores the importance of stringent fire safety measures within healthcare premises.

NABH, being National Accreditation body for healthcare organizations in India, mandates compliance with rigorous fire safety standards to mitigate risks and uphold the highest standards of patient care and staff safety. Adherence to these standards not only safeguards lives but also contributes to maintaining operational continuity and preserving essential healthcare services.

The Ministry of Health, Government of India, has issued aa advisory emphasizing the imperative for HCOs to prioritize fire safety measures. It is incumbent upon all healthcare establishments to take due cognizance of this directive and implement comprehensive fire safety protocols without delay. We are enclosing aforesaid advisory vide notification no. HFW/Advisory to prevent hospital fires/23rdMarch2024/1, dated 23 March 2024, appended as Annexure 1, for the reference of all our health care partners.

In light of this, all HCOs are reminded to:

- Conduct regular fire risk assessments and audits to identify vulnerabilities and ensure compliance with fire safety regulations.

- Implement robust fire prevention measures, including proper storage of flammable materials, maintenance of electrical systems, and installation of fire detection and suppression systems.

- Provide regular training to staff members on fire evacuation procedures, including the safe evacuation of patients with special needs.

- Establish clear communication channels and emergency response protocols to coordinate effectively in the event of a fire or other emergencies.

- Periodically review and update fire safety policies and procedures to address emerging risks and incorporate best practices.

Page No. 01 of 10

Failure to prioritize fire safety not only jeopardizes lives but also poses legal and reputational risks to healthcare organizations. NABH urges all HCOs to demonstrate unwavering commitment to fire safety and incorporate it as an integral component of their quality assurance framework

For further guidance and support on implementing fire safety measures, HCOs are encouraged to refer to

NABH's Advisory for Minimum Essential Fire Safety Measures available on our website, enclosed as Annexure 2. These guidelines are meant to ensure patient safety and in no way absolves the organization of fulfilling its statutory obligations with regard to fire safety.

https://nabh-portal-live.s3.ap-south-1.amazonaws.com/wp-content/uploads/2025/07/24130821/RevisedAdvisory-for-Minimum-Essential-Fire-Safety-Measures-20.09.2022.pdf

For additional information and compliance by applicants and accredited healthcare establishments in Delhi, the National Accreditation Board for Hospitals & Healthcare Providers (NABH) hereby notifies the updated guidelines on the applicability of the Fire Safety Compliance Certificate, enclosed as Annexure 3.

Let us collectively uphold the highest standards of safety and quality in healthcare delivery

Thanking you,

Sincerely yours,

(Dr. Atul Mohan Kochhar)

CEO-NABH

Documents Enclosed:

Annexure 1: Advisory to prevent hospital fires from Ministry of Health, Government of India

Annexure 2: NABH's Advisory for Minimum Essential Fire Safety Measure

Annexure 3: Applicability of Fire Safety Compliance Certificates in Delhi

Page No. 02 of 10

ANNEXURE 1

www.pib.gov.in

PRESS INFORMATION BUREAU GOVERNMENT OF INDIA

*****

As temperatures escalate, Union Health Ministry and NDMA Issue Joint- Advisory to States on measures to prevent Hospital Fires during Summer months

States/UTs directed to ensure all accredited hospitals within their jurisdiction conduct thorough inspections, address discrepancy in electrical load capacity and obtain valid fire NOCs from respective state fire departments

States/UTs also urged to conduct follow-up reviews to ensure implementation of critical safety measures

New Delhi, 23 March 2024

As temperatures escalate during the summer months, hospital fires become a significant threat. To prevent this, the Union Health Ministry and the National Disaster Management Authority (NDMA) have issued a joint advisory to all States/UTs underscoring the paramount importance of proactive measures in preventing such devastating incidents.

State Health Departments and State Disaster Management Authorities have been directed to work in close collaboration to ensure that all accredited hospitals within their jurisdiction take immediate action on the following:

- Thorough Inspections: Conduct comprehensive fire safety audit / on-site inspections of all hospitals to assess fire safety compliance. Ensure that fire-fighting systems, including fire alarms, fire smoke detectors, fire extinguishers, fire hydrants,and fire lifts, are present and fully functional.

- Electrical Load Audits: Address the critical issue of insufficient electrical load capacity. Hospitals must regularly conduct electrical load audits, particularly when adding new equipment or converting spaces into ICUs. Any identified discrepancies must be promptly rectified.

- Fire NOC Compliance: Hospitals must strictly adhere to regulatory requirements and obtain valid fire No-Objection Certificates (NOCs) from their respective state fire departments. Prioritize re-calibration of electrical loads in older buildings constructed before adopting fire safety norms.

A detailed set of instructions outlining the steps and measures to be undertaken by hospitals to ensure fire safety compliance have also been provided to Chief Secretaries of all States and UTs, recommending them to disseminate the information among all accredited hospitals.

Page 3 of 10

Following are the instructions that need to be carried out to prevent occurrences of fire incidents in hospitals and other healthcare facilities:

- Functional Fire-Fighting Systems: Hospitals must regularly inspect fire- fighting equipment such as fire extinguishers, hydrants, and alarms. This includes checking the expiry dates of extinguishers, ensuring hydrants are accessible and have adequate water pressure, and that fire alarms are operational and audible throughout the facility.

- Regular Maintenance and Testing: Establish a maintenance schedule for all Are safety equipment. This should include monthly checks of fire extinguishers, quarterly tests of fire alarms and hydrants, and annual professional inspections to certify their effectiveness in accordance with relevant Indian Standards.

- Regular Electrical Load Audits: Conduct electrical audits bi-annually to evaluate the hospital's power consumption, particularly in high-demand areas like ICUs. Upgrades or modifications should be assessed by a certified electrician to ensure they meet safety standards without overloading the system as per the National Electrical Code of India-2023.

- Oxygen Safety: In areas with oxygen tanks or piped oxygen, implement strict no-smoking policies and controls on heat sources. Signage should clearly mark these areas, and staff should be trained on the risks associated with high- oxygen environments.

- Installation of Smoke Detectors and Fire Alarms: Ensure fire smoke detectors and fire alarms are installed in all hospital areas, particularly in patient rooms, hallways, and common areas. Test these systems montly as stipulated in IS2189 and replace batteries annually or as needed.

- Combustible Material Control: Audit materials used in hospital construction and furnishings to identify and replace combustible materials with non-combustible or fire-resistant alternatives, especially in-patient care areas.

- Non-Combustible MateriaI for Electrical Ducts: Inspect electrical ducts to ensure they are sealed with materials like intumescent firestop sealants that prevent the spread of fire and smoke through openings.

- Avoid Overloading Power Sources: Use power management systems to monitor electrical loads and prevent overloading. Ensure that multiple high- power devices are not connected to a single circuit. Regularly review power distribution to accommodate new equipment safely.

- Installation of Water Sprinklers and Hosepipes: Fit critical areas, including ICUs and operation theatres, with automatic sprinkler systems and accessible hosepipes. These systems should be linked in sync with the fire alarm system to be activated in the event of a fire.

- Strict Adherence to the National Building Code: Regularly review and update hospital infrastructure to comply with the latest fire safety standards outlined in the National Building Code 2016. This includes ensuring proper ventilation systems, fire-resistant doors, and emergency lighting in corridors and stairwells.

- Obtaining Fire Safety NOC: Annually Renew the Fire Safety No-Objection Certificate as per State Fire Safety Rules from the local fire department. This includes submitting up-todate fire safety plans and records of equipment maintenance and staff training.

- Staff Training and Drills: Implement a continuous training program for all staff on fire prevention, emergency procedures, and the use of fire-fighting equipment. Conduct biannual fire drills, including evacuation drills, to ensurestaff, doctors, and patients know how to respond in an emergency.

- Evacuation Plans: Develop comprehensive evacuation plans that include clear, well-marked escape routes, emergency exits free of obstructions, and designated safe assembly areas. Plans should be displayed prominently throughout the hospital and in staff training programs. Each hospital has to formulate an SoP to be followed in case of a fire incident.

States/UTs have also been urged to conduct follow-up reviews to ensure the implementation of these critical safety measures.

*****

MV

## HFW/Advisory to prevent hospital fires/23rdMarch2024/1

NATIONAL ACCREDITATION BOARD FOR HOSPITALS AND HEALTHCARE PROVIDERS ANNEXURE 2

Advisory for Minimum Essential Fire Safety Measures

Applicable to Healthcare Units under all schemes of Certification and Accreditation These guidelines are meant to ensure patient safety and in no way absolves the organization of fulfilling its statutory obligations with regard to fire safety.

Present

Absent

Verify that minimum essential

fire

safety

measures

are

in

place

and or functioning

Approval/Registration

from

local

health authority Eg: Nursing

home Act/DHO

If Fire NOC is not applicable, organization to

provide

justification for the same.

If Fire NOC is applicable, confirm that the

organization has applied for fire NOC and

there

is

regular

correspondence

(

at

least

once

in

three

months)

with

fire

department

which

is

acknowledged.

Any

correspondence

received

from

the fire department has to be submitted

In absence of Fire NOC, *Third party

inspection

certificate

should

be

available.

The

third

-

party audit should provide evidence to

suggest that statutory norms are adhered to.

Any

Observation by the third party should

have been addressed.

The

third

-

party

inspection

certificate

is

valid

for

a maximum period of one year

Head of

the

organization/Promoter

to

give an

undertaking on the organization’s letter

-

head

stating that fire

safety measures are in place

and adhered to at all times.

During

assessment,

verify

that

the

points

in

the checklist are in place and are

functioning

Valid Fire NOC

National Accreditation Board for Hospitals and Healthcare Providers, Dated 20th September 2022

## NATIONAL ACCREDITATION BOARD FOR HOSPITALS AND HEALTHCARE PROVIDERS

*NABH prescribes that Fire & Life Safety Inspection Certificates under NABCB accreditation issued by NABCB accredited Type ‘A’ Inspection Bodies for Fire & Life Safety Inspections of hospitals/health care providers shall be in accordance with the following:

- National Building Code of India

- Model Bill to provide for the maintenance of Fire and Emergency service for the state (2019) c. Respective State Fire Safety Rules

- NABH accreditation requirements for fire safety and applicable statutes

- Any other applicable statutes.

Such Fire & Life Safety Inspection Certificates shall be accepted in lieu of statutory Fire NOC, only for consideration for the purpose of NABH accreditation. This does not absolve the hospitals/health care providers from complying to Fire NOC requirements/any other extant applicable statutes. It shall be sole responsibility of hospitals/health care providers to obtain Fire NOC, as applicable.

NABCB accredited Inspection Bodies shall be required to issue a final Fire & Life Safety Inspection certificate under NABCB accreditation bearing NABCB Accreditation Mark after the inspection is carried out and satisfactory corrective action and resolution of non-conformities, if any.

NABH accreditation requirements for Fire & Life Safety : (in addition to above)

- Firefighting equipment like wet riser, hydrants, auto sprinkler, fire alarm system, fire extinguishers of all types and sizes should be available as per table below (adapted from NBC 2016).

- Operational and maintenance plan for firefighting equipment including refilling of extinguishers.

- Up to date fire drawings to be available. Where applicable, the fire drawings should also specify the location of fire dampers.

- Fire detection and smoke detectors exist across all floors. The detectors shall be tested for functionality at regular intervals, and records maintained.

- Central fire alarm system is installed at a location which is staffed 24/7.

- Fire exit plan for each floor. Exit door should be openable and free from any materials whichwill obstruct way.

- Fire Exit signage on all floors well illuminated/ self-glowing, as per NBC guidelines.

- Emergency illumination system in case power goes.

- Designated place for assembly of patients and staff in case of fire.

- Mock fire drill records and schedule of conduct of drills.

National Accreditation Board for Hospitals and Healthcare Providers, Dated 20th September 2022

## NATIONAL ACCREDITATION BOARD FOR HOSPITALS AND HEALTHCARE PROVIDERS

Minimum Requirements for Fire Fighting Installations

| Type of Hospital | Wet Riser | Automatic Sprinkler | Manually operated electricfire alarm | Auto detectionand fire alarm system |
| --- | --- | --- | --- | --- |
| Hospitals less than 15 meters in height, with plot area upto 1000 square metres and upto G + 1 floor | NR | R | R | NR |
| Hospitals less than 15 meters in height, with plot area upto 1000 square metres and G + 2 floors | R | R | R | R |
| Hospitals less than 15 meters in height withplot area more 1000 square metres | R | R | R | R |
| Hospitals 15 meters and above but not exceeding 24 meters in height | R | R | R | R |
| Hospitals above 24 meters but not exceeding 45 meters in height | R | R | R | R |
| R = Required NR= Required Sufficient water storage (underground and/or terrace) should be provided to ensure fire-fighting |  |  |  |  |

National Accreditation Board for Hospitals and Healthcare Providers, Dated 20th September 2022

## NATIONAL ACCREDITATION BOARD FOR HOSPITALS AND HEALTHCARE PROVIDERS

ANNEXURE 3

Applicability of Fire Safety Compliance Certificates in Delhi

The National Accreditation Board for Hospitals & Healthcare Providers (NABH) hereby informs all applicant and accredited healthcare establishments in Delhi about the updated guidelines regarding the applicability of the Fire Safety Compliance Certificate.

It provides important insights into the applicability of Fire Safety Compliance (FSC) Certificates, including Fire No Objection Certificates (NOC), for various healthcare and business establishments. These guidelines are based on Part IV of the National Building Code (NBC) 2016 guidelines, ensuring that fire safety protocols align with regulatory standards.

- Day Care Establishments (e.g., Eye Centres, Dental Clinics, OPDs, Diagnostic Labs, Dialysis Centres):

If these establishments do not provide sleeping or overnight facilities for patients, they fall under the category of Business Occupancy. These businesses are permitted to operate in the buildings having single basement (below 200 SQM) and ground plus 03 stories, height below 15 m. However, use of the basement shall be subject to the approval from local building authority i.e MCD, NDMC.

- Business Buildings Below 15 Meters in Height:

Business buildings that are less than 15 meters height or ground plus 3 stories are exempt from requiring a Fire NOC/FSC.

- Business Buildings Above 15 Meters in Height:

Business buildings exceeding 15 meters in height are required to obtain a Fire NOC/FSC.

- Nursing Homes/Hospitals Below 9 Meters in Height or Ground Plus One Floor (including   Mezzanine):

Nursing homes or hospitals with a height of 9 meters or less, or those operating in the buildings having single basement (below 200 SQM) and ground plus 01 Stories, are not required to obtain a Fire Safety Certificate. (Basement area should be less than 200 sqm).

- Nursing Homes/Hospitals Between 9 to 15 Meters in Height:

Nursing homes or hospitals with a height between 9 and 15 meters, or buildings that include a basement and ground plus 03 upper floors, where the hospital operates in the basement, ground floor, and first floor, while the second & third floors are either used for residence of doctors, or not utilized for hospital operations, or are sealed off, are not required to obtain a Fire NOC/FSC.

Page 9 of 10

- Basements in Nursing Homes/Hospitals: Basements in nursing homes or hospitals cannot be used to house inpatient facilities or operate as operating theatres/ cath lab. Buildings having double basements need to obtain fire safety certificate as per clause 7.4.12 of UBBL 2016. For basement of size more than 200 SQM, fire safety measures as per NBC Part IV shall be provided.

- Home Care and Palliative Care Centres: All home care and palliative care centres are also to be treated as Institutional buildings same as nursing homes as explained above.

- Third-Party Fire Safety Audit Reports: Reference NABH Fire Safety guidelines published on the website of NABH. Fire safety audits conducted by third parties should comply with the guidelines specified in the National Building Code (NBC)-Part IV 2016.

- Documents to be Submitted by Healthcare Organizations When Fire NOC is Not Applicable:

  - Third-Party Fire Safety Audit Reports:

Healthcare organizations must submit fire safety audit reports conducted by third-party agencies. These audits should comply with the standards outlined in the National Building Code (NBC)-Part IV 2016.

  - Geo-Tagged time stamped Photographs for Third-Party Auditors:

Third-party auditors are required to include geo-tagged time stamped photographs of the healthcare facility along with their audit report to verify the location and condition of the premises.

  - Affidavit on Building Height and Fire Safety Compliance:

An affidavit must be provided, declaring the building’s height and confirming that the facility consistently adheres to fire safety norms as mandated by relevant regulations.

  - Day Care Establishments (e.g., Eye Centres, Dental Clinics, OPDs, Diagnostic Labs, Dialysis Centres) – Basement Use Approval from Local Building Authorities (e.g., MCD, NDMC):

Day Care Establishments (e.g., Eye Centres, Dental Clinics, OPDs, Diagnostic Labs, Dialysis Centres) must submit approval for the use of the basement from the relevant local building authorities, i.e MCD or NDMC, as outlined in point 1.

## 10. Verification of Fire NOCs: The authenticity of Fire NOCs issued by the Fire Department can be verified on the Fire Authority's official website

NABH urges all healthcare facilities to ensure compliance with these updated fire safety guidelines to enhance safety and meet accreditation requirements.

We emphasize the importance of prioritizing fire safety to safeguard the well-being of patients, staff, and visitors in healthcare facilities. NABH remains committed to supporting healthcare providers in upholding the highest standards of safety and compliance.

Page 10 of 10